[image: image1.png]r
517 2?0

i . T

1 e i




                                            户外空调直流器

                                                          Cabinet DC Air Conditioner

产品简介
应用范围
本产品广泛应用于户外通讯机柜、电池柜、电气柜、工业控制柜等需要散热 的场合.

[image: image4.jpg]#)SAN DA



设计专长
 全部配置直流器件，真正的全直流空调；

 矢量变频，精确控温；

 宽电压设计：DC42～60V，适合范围更广；

 完善的运行逻辑，避免了对供电系统的冲击；

 完美的低能耗设计，能效比（EER） ≥ 2.5,季节能效比（SEER） ≥ 4.5；

 相比同类交流型号产品节能率高达50%；

 IP55防护等级、适合T3高温工况、R134a环保制冷剂；

 太阳能、风能、油机等新能源混合供电系统中完美的冷却散热解决方案；

 精湛工艺及高质量国际名牌配件确保产品更加稳定可靠；

 多重保护功能；

 干接点告警输出，常开/常闭可选；

 配置有通讯接口:RS485(YD/T 1363.3协议)；

Product Introduction
Range of application
 This series product can be widely used in enclosed area for climate control, such as wireless communication cabinet, battery cabinet,industry control cabinet etc;
Product Design Feature
 Designed with all DC driven components like fans, compressor;

 Precise temperature control through inverter digital regulation of compressor, fans;
 Power supply voltage range: DC42~60 V ;
 A comprehensive sell-protection design to realize partial load starting, partial load operation at severe ambient condition;
 Low power consumption design with EER≥2.5, SEER≥ 4.5;
 Energy saving reach to 50% comparing with A.C. version product;
 IP55 environment protection & fit for T3 high temperature working condition by using of R134a refrigerant gas;

 The best cooling solution for solar, wind, disel generator etc,hybrid power system;

 Strict process control and international brand parts deployed to ensure high quality and reliable of this product;

 Multiple self protection design;
 Dry contact alarm output,NO/NC optional;

 Equipped with communication interface:RS485(YD/T 1363.3 Modbus communication protocol ).

技术参数/Technical Parameters

	产品名称
	Name
	户外机柜空调器/Outdoor Cabinet Air Conditioner

	型号
	Model
	SDCA 030 /N/D/D

	固定方式
	Mounting Method
	半嵌入/Semi-embedded  Mounting

	电源
	Power Supply
	-48V DC

	制冷量
	Cooling Capacity
	3000W@L35/L35

	功耗
	Power Consumption
	960W@L35/L35

	制冷量
	Cooling Capacity
	1800W@L35/L55

	功耗
	Power Consumption
	1350W@L35/L55

	内循环风量
	Internal Airflow
	850 m³/h

	工作温度范围
	Working Temperature Range
	-40℃~+55℃

	最大噪音
	Max Noise Level
	65dB(A)

	IP等级
	IP Grade
	IP55

	净重
	Net Weight
	60kg

	制冷剂
	Refrigerant
	R134a

	外形尺寸
	Dimensions
	1154x489x225(mm,HxWxD)

	CE和环保
	CE&RoHS Compliant
	符合/YES

	表面处理
	Surface Treatment
	Outdoor type powder coating,standard color: RAL7035

	加热器
	Heater
	可选择(1000W) / Optional(1000W)


冷量曲线/Cooling Capacity Chart                 功耗曲线/Power Consumption Chart 

[image: image5.png]L

T




[image: image6.png]3 #£/Power Consumption(W)

1650

1500

1350

1200

1050

900

750

500

350

200

@

@

20 25 30 35 40 45 5

0 5

5

I35 £ /Ambient Temperature(C)

60

1 PR €]
Cabinet Inside Temperature ®






外形尺寸/Product Dimension

[image: image9.png]s O K3




安装说明/ Installation instructions

图1-柜门开孔尺寸                             图2-防护罩建议结构
Figure 1-Cabinet Door Cutting Dimension      Figure 2-Air open design of cowling
[image: image2.png]%44MER +HOuter Dimension)

1154

1182
4175 /Outer Dimension)

4x280=1120

280

S
I

HSOFFAL

[ Bhaust air outlet open

FIFLEES] OFILE=T5%)
Round hole array
Percentage of open area >75%)





图3-安装示意图

Figure3-Installation Instruction

[image: image3.png]



注意： 1.本系列空调不需要安装防护罩,如果客户确实想安装防护罩,请遵循以下规则: 1.防护罩由客户自备,防护罩的设计请参考图2；
防护罩进风口和出风口开孔面积应足够大,以确保足够的循环风量，这对于延长空调的使用寿命和减少维护频率非常的重要；

3.防护罩的进出风口应该防止气流短路,以便空调可以获得最佳的冷却效果。

Attention:
1.This series air conditioner does not need a cowling, if customer does want to put a cowling outside unit, please follow below rules: 1.The cowling can be made by customer self, the design of cowling please refer to figure 2
2.The inlet and outlet open for ambient air in and exhaust air out should be big enough to ensure enough air volume circulation. This is very important to have the air conditioner running with long lifetime and less service.
3.When you make a cowling design/installation, make sure the inlet air and outlet air not been short cut, this is also critical to keep unit have best cooling performance.
接线端子说明/Terminal instructions

手操器使用说明：

[image: image7.png]#)%#/Cooling Capacity(W)

4400

4000
3600 ®
3200
2800

»
2400 [@ \\
2000
1600
1200
800
400

20 25 30 35 40 45 50 55 6

3L 35 £ /Ambient Temperature(C)
18 PR @-——25C
Cabinet Inside Temperature (o — 35C




在正常情况下，手操器显示柜内温度，告警时显示告警代码；手操器底部为状态栏，不同的指示灯代表不同状态：

[image: image8.png]oMo

A+ B- NC COR I/0

BEEEH

RTE -48V PE




：闪烁表示空调处于自检状态或温度设置状态；

：闪烁表示空调即将进行制冷；常亮表示空调正在进行制冷；

：常亮表示空调正在进行制热；

：常亮表示外风机正在运行；

：闪烁表示告警发生；

Instructions of display panel:
The display panel shows cabinet temperature under normal circumstance. and shows alarm code when there is a malfunction.
In the bottom is the status bar,different lamp represents different status.
：Flashing when self diagonse or temperature setting mode.
：Lamp on when cooling;
：Lamp on when heating;
：Lamp on when external fan is running;

：Flashing when alarm.
	序号 / Number
	符号 / Symble
	定义 / Definition
	描述 / Description

	1
	RTE
	直流电源正极Positive pole of DC power
	/

	2
	-48V
	直流电源负极Negative pole of DC power
	/

	3
	PE
	直流电源地线Ground wire of DC power
	/

	4
	A+
	RS485通讯正极

Positive pole of 485 communication
	/

	5
	B-
	RS485通讯负极Negative pole of 485 communication
	/

	6
	NC
	干接点告警常闭端口

Normal closed port of dry contract alarm output
	干接点告警：

6、7端口：干接点告警常闭状态。

Dry contact alarm;

Pin6&7:Normal closed

	7
	COM
	干接点告警公共端口

Common port of dry contract alarm output
	

	8
	I/O
	外部控制输入端口

external signal input port
	外部控制输入接口:接受外部控制信号来控制空调。

As external singal input port:

Accept external control signal to control the air

conditioner.



	9
	
	
	


Zhuzhou Sanda Electronic Manufacturing Co.,Ltd 

ADD: Wuli Dun Industry Zone, Liling, Zhuzhou, Hunan, China         

Mobile/Skype/Whatsapp: +86 188 7473 1668

Email: sanda09@digitalmeter-suppliers.com   http://sandaenvicool.com/ 

