[image: image1.png]468

788
632

20 68|,

68 [ a1 &2
s

280




                                            户外空调交流器

                                                          Cabinet AC Air Conditioner

产品简介
应用范围
[image: image4.jpg]#)SAN DA



本产品广泛应用于户外通讯机柜、电池柜、电气柜、工业控制柜等需要散热 的场合.

设计专长
 实现遥测、遥信、遥调，可实现多重自动保护和全面的故障自诊断功能；

 精湛工艺及高质量国际名牌配件确保产品更加稳定可靠；

 适合T3高温工况、R134a环保制冷剂；

 多重保护功能、可视化人机界面、RS485接口(MODBUS-RTU)；

 LED数码管显示，现场参数可设置；

 加热功能、排氢功能可选；

 干接点告警输出，常开/常闭可选；

 安全防盗，无需增加防护罩。

Product Introduction
Range of application
 This series product can be widely used in enclosed area for climate control, such as wireless communication cabinet, battery cabinet,industry control cabinet etc;
Product Design Feature
 Remote measuring, remote communication, remote control, which can realize multiple automatic protection and comprehensive self-testing function;
 Strict process control and famous brand components to ensure high quality and reliability of this product;
 Fit for harsh condition (T3), R134a refrigerant ;
 Multiple self-protection design & visible monitoring interface, RS485 communication port (MODBUS-RTU protocol);
 LED display, all the settings can changed at the field;
 The heating function and the hydrogen function is optional;
 Dry contact alarm output,NO/NC optional; Anti-theft design, without  the cowling.

技术参数/Technical Parameters

	产品名称
	Name
	户外机柜空调器/Outdoor Cabinet Air Conditioner

	型号
	Model
	SDCA 010/N/D/A

	固定方式
	Mounting Method
	半嵌入/Semi-embedded  Mounting 



	电源
	Power Supply
	230VAC±15%  50Hz

	制冷量
	Cooling Capacity
	1050W@L35/L35

	功耗
	Power Consumption
	540W@L35/L35

	制冷量
	Cooling Capacity
	620W@L35/L55

	功耗
	Power Consumption
	650W@L35/L55

	内循环风量
	Internal Airflow
	400 m³/h

	工作温度范围
	Working Temperature Range
	-40℃~+55℃

	最大噪音
	Max Noise Level
	63dB(A)

	IP等级
	IP Grade
	IP55

	净重
	Net Weight
	30kg

	制冷剂
	Refrigerant
	R134a

	外形尺寸
	Dimensions
	783x479x200(mm,HxWxD)

	CE和环保
	CE&RoHS Compliant
	符合/YES

	表面处理
	Surface Treatment
	Outdoor type powder coating,standard color: RAL7035

	加热器
	Heater
	可选择(1000W) / Optional(1000W)

	排氢功能
	Hydrogen Function
	可选择/ Optional


[image: image5.png]


冷量曲线/Cooling Capacity Chart                 功耗曲线/Power Consumption Chart 

[image: image6.png]ThkE/Power Consumption(W)

850

800

750

700

650

600

550

500

450

00
20 25 30 35 40 45 50 55 60

15 B/Ambient  Temperature(C)

TriEE @---25C
[cabinet Inside Temperature @----35C






外形尺寸/Product Dimension

[image: image9.png]s O K3




安装说明/ Installation instructions

图1-柜门开孔尺寸                             图2-防护罩建议结构
Figure 1-Cabinet Door Cutting Dimension      Figure 2-Air open design of cowling
[image: image2.png]479(% 841 )R /Outer Dimension)

468

260

12-26

749

WEBAIR
Cutoff the shadow

632

768
T /Outer Dimension)

|21

210

e8]

783( TSNP

83888588383838585883338383 |
83858588383838585858833383

HROFFL

[ Exhaustairoutiet open

BTLEE5) OF L% =T5%)
Round hole amay
Percentage of open area 75% )

SRR O

Ambient air inlet open

LIS

The louvers structure




图3-安装示意图

Figure3-Installation Instruction

[image: image3.png]



注意： 1.本系列空调不需要安装防护罩,如果客户确实想安装防护罩,请遵循以下规则: 1.防护罩由客户自备,防护罩的设计请参考图2；
防护罩进风口和出风口开孔面积应足够大,以确保足够的循环风量，这对于延长空调的使用寿命和减少维护频率非常的重要；

3.防护罩的进出风口应该防止气流短路,以便空调可以获得最佳的冷却效果。

Attention:
1.This series air conditioner does not need a cowling, if customer does want to put a cowling outside unit, please follow below rules: 1.The cowling can be made by customer self, the design of cowling please refer to figure 2
2.The inlet and outlet open for ambient air in and exhaust air out should be big enough to ensure enough air volume circulation. This is very important to have the air conditioner running with long lifetime and less service.
3.When you make a cowling design/installation, make sure the inlet air and outlet air not been short cut, this is also critical to keep unit have best cooling performance.
接线端子说明/Terminal instructions

手操器使用说明：

[image: image7.png]#il#4it/Cooling Capacity(W)

0

1800
1600
1400
1200

B
1000
800
600
~
400
200
0
50 B!

4% B/Ambient  Temperature(tT)

TRrVEE @---25C

|Cabinet Inside Temperature @----35C




在正常情况下，手操器显示柜内温度，告警时显示告警代码；手操器底部为状态栏，不同的指示灯代表不同状态：

[image: image8.png]o

A+ B- NC COR I/0

o

BT

LW PE



：闪烁表示空调处于自检状态或温度设置状态；

：闪烁表示空调即将进行制冷；常亮表示空调正在进行制冷；

：常亮表示空调正在进行制热；

：常亮表示外风机正在运行；

：闪烁表示告警发生；

Instructions of display panel:
The display panel shows cabinet temperature under normal circumstance. and shows alarm code when there is a malfunction.
In the bottom is the status bar,different lamp represents different status.
：Flashing when self diagonse or temperature setting mode.
：Lamp on when cooling;
：Lamp on when heating;
：Lamp on when external fan is running;

：Flashing when alarm.
	序号 / Number
	符号 / Symble
	定义 / Definition
	描述 / Description

	1
	L
	交流电源火线Live line of AC power
	/

	2
	N
	交流电源零线Neutral line of AC power
	/

	3
	PE
	交流电源地线Ground wire of AC power
	/

	4
	A+
	RS485通讯正极

Positive pole of 485 communication
	/

	5
	B-
	RS485通讯负极Negative pole of 485 communication
	/

	6
	NC
	干接点告警常闭端口

Normal closed port of dry contract alarm output
	干接点告警：

6、7端口：干接点告警常闭状态。

Dry contact alarm;

Pin6&7:Normal closed

	7
	COM
	干接点告警公共端口

Common port of dry contract alarm output
	

	8
	I/O
	排氢或外部控制输入端口

Hydrogen discharging port or

external signal input port
	排氢接口或外部控制输入,

两个功能只能选其一：

做为排氢接口：接排氢风机（交流或直流风机）

排氢风机的电流应小于1A；

做为外部控制输入接口:接受外部控制信号来控制空调。

Hydrogen discharging or external signal input port

both can only choose one:

As hydrogen port:

Can connect external hydrogen exhaust fan(AC&DC).

Current of hydrogen exhaust fan should be less than 1 A

As external singal input port:

Accept external control signal to control the air

conditioner.



	9
	
	
	


Zhuzhou Sanda Electronic Manufacturing Co.,Ltd 

ADD: Wuli Dun Industry Zone, Liling, Zhuzhou, Hunan, China         

Mobile/Skype/Whatsapp: +86 188 7473 1668

Email: sanda09@digitalmeter-suppliers.com   http://sandaenvicool.com/ 

